## Slide 1
INTEGRACIJA SOLAR-TERMAL POTROJENJA SA SEZONSKIM SKLADIŠTEM TOPLOTE U SISTEM DALJINSKOG GREJANJA NOVOG SADA
Stručno-naučna konferencija TOPS 2025, Zlatibor Vladimir Munćan, Igor Mujan, Aleksandar Anđelković, Dušan Macura

## Slide 2: Solar-thermal novi sad: system design

## Slide 4: System overview

## Slide 5: System overview

## Slide 6: How does it work?
Main components:
Solar thermal collector field
PTES – Pit thermal energy storage
Electric Boiler - eBoiler
electrical Heat pump
Water intake from Danube river
TE-TO - Efficient CHP
DH Network pipeline
GRS – Existing District Heating System

## Slide 7
Non-heating season (CHARGING PTES)

## Slide 8
heating season

## Slide 9
Yearly heat flow

## Slide 10: PTES Design
Volume of North: 383,186 m³
Volume of South: 486,661 m³
Charge/discharge: 106 MW

## Slide 11
PTES Cross section

## Slide 12
Floating liner
Bottom layer
Middle layer
Top layer
Insulation
Ballast
PTES LID

## Slide 13: PTES Construction - Lining of sides and bottom

## Slide 14
PTES Construction - Protection liner

## Slide 15
PTES Construction - Filling storage with water

## Slide 16
PTES Construction - Installation of floating liner

## Slide 17
PTES Construction - Installation of floating liner

## Slide 18
PTES Construction - Installation of insulation layers

## Slide 19
PTES Construction - Ballast installed

## Slide 20: Solar thermal FIELD
Collector area: 38,623 m²
Collectors: 2420
Yearly production: 29,067 MWh

## Slide 21
Technical Specifications | Value | Unit
Total gross collector area | 38,623 | [m²]
Number of solar collectors | 2,420 | [-]
Approximate land footprint | 74,172 | [m²]
Secondary side temperatures (return) | ~10 | [°C]
Collector installation angle | 30 | [°]
Collector azimuth angle | 0 | [°]
Distance between collector rows | 5 | [m]
Solar field operating heat transfer fluid (HTF) | 30% Propylene Glycol / Water | [-]
solar FIELD

## Slide 22
Solar Field Specifications | Value | Unit
Peak thermal output (gross) | 31,21 | [MWth]
Annual thermal yield (gross - reference year) | 29,067 | [MWhth]
Annual thermal yield (net - reference year) | 28,195 | [MWhth]
Maximum expected daily thermal yield (gross) | 220.54 | [MWhth]
solar FIELD Performance Simulation

## Slide 23
solar thermal plant

## Slide 24: Heat pump station
Heating power: 17 MW
COP: 3.49
Dual source
Output temperature: 90 °C

## Slide 25
Non-heating season
Heat from Danube
Heat to PTES
Heating season
Heat from PTES
Heat to Novi Sad
HEAT PUMP Operating principle

## Slide 26: Electric boiler
Thermal power: 2x30 MW
Voltage: 20 kV
Efficiency: >99%

## Slide 27
eBOILER OPERATING PRINCIPLE

## Slide 28: Summary

## Slide 29
Summary - ENERGY BALANCE
Heat Balance | Total [GWh]
Heat Demand (North+East+South) | 478
Solar thermal to PTES | 22
Heat pump to PTES | 44
Eboiler to PTES | 39
TeTo to PTES | 133
River Danube to HP | 28
PTES to HP | 40
Electricity to HP | 33
PTES heat loss | 23
PTES to GRS | 182
Solar thermal to GRS | 7
Heat pump to GRS | 54
TeTo to GRS (Heat supply from TeTo) | 230
Heat supply from local boilers (North+East+South) | 20

## Slide 30
Summary - COST BENEFIT ANALYSIS
EBRD Financing:
Sovereign loan of EUR 80 million to Republic of Serbia
Co-financed by EUR 25 million investment grant from the European Union through the Western Balkans Investment Framework (WBIF)
On 27 December 2024, the Loan Agreement and the Project Agreement for the financing of the Solar-Thermal Novi Sad project were signed.
The project implementation is planned for the period 2026–2028.
Overall CAPEX - Solar-thermal Novi Sad | 
PTES | 48.850.000
Solar thermal field | 11.900.000
Heat pump system | 12.877.500
River water supply and filtration at TE-TO | 4.235.000
eBoilers Plant | 4.650.000
Transformer and electrical connection for E-boilers | 2.500.000
Technical Building | 4.005.000
Technical installation | 6.187.400
Works and supplies | 95.204.900
Contingency (10%) | 9.520.490
Total | 104.725.390
Scenario with grant financing |  | 
EIRR | % | 12%
ENPV | EUR | 40,083,333
E. Payback Period | years | 9

## Slide 31
Hvala na pažnji!
Dušan Macura
dusan.macura@nstoplana.rs